## SUB_INDEX
|  | HEAT TRANSFER PRODUCTS GROUP, LLC |  | SUBMITTAL DATA INDEX
|  | 3885 Crestwood Parkway / Suite 500 |  | Model Series - RDS / RDD
|  | Duluth, GA 30096 |  | QUANTUM AIR
(P) 800-288-9488 / (F) 256-259-7478
|  | http://russell.htpgusa.com |  | Remote - Air Cooled Condenser
LEFT CLICK ON UNIT MODEL NUMBER LISTED BELOW FOR THE APPLICABLE SUBMITTAL SHEET
SUBMITTAL DATA INDEX
VSEC 900 RPM
|  | SINGLE WIDE MODELS | DOUBLE WIDE MODELS
|  | RDS004*G1A | RDD020*G2A
|  | RDS005*G1A | RDD028*G2A
|  | RDS007*G1A | RDD032*G2A
|  | RDS010*G2A | RDD042*G3A
|  | RDS014*G2A | RDD049*G3A
|  | RDS015*G2A | RDD056*G4A
|  | RDS021*G3A | RDD065*G4A
|  | RDS025*G3A | RDD070*G5A
|  | RDS028*G4A | RDD087*G5A
|  | RDS033*G4A | RDD105*G6A
|  | RDS035*G5A | RDD122*G7A
RDS044*G5A
RDS052*G6A
RDS061*G7A
MODEL NUMBER KEY
R D S 004 E G 1 A
A = Revison Code
R = Russell
# Fans Long
1 thru 7
| D = Condenser |  |  | Motor RPM/TYPE
G = 900 / VSEC
S = Single Wide
D = Double Wide
Voltage Code
| Capacity = MBH / THR |  |  | E = 208/230/3/60
| Per Degree TD / 10 FPI |  |  | G = 460/3/60
N = 200/220/3/50
Q = 380/3/50
900 RPM VSEC 01/24/25 CB

## RDS004_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 3.7 | 4.1 | 4.3 | 4.7
|  |  | R-407A ^ | 3.3 | 3.7 | 3.9 | 4
|  |  | R-448A ^ | 3.3 | 3.7 | 3.9 | 4
|  |  | R-449A ^ | 3.3 | 3.7 | 3.9 | 4
|  |  | R-407C ^ | 3.234 | 3.626 | 3.822 | 3.92
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TY[E | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | VSEC | 900 | 9000 | 1-1/8" | 7/8" | 63.5 | 4.5 Lb's | 16.7 Lb's | 400 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.2 | 7 | 15 | 15
|  |  | 460 | 3 | 1.2 | 2.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS005_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 5.1 | 5.6 | 5.9 | 6.5
|  |  | R-407A ^ | 4.7 | 5.2 | 5.5 | 5.7
|  |  | R-448A ^ | 4.7 | 5.2 | 5.5 | 5.7
|  |  | R-449A ^ | 4.7 | 5.2 | 5.5 | 5.7
|  |  | R-407C ^ | 4.606 | 5.096 | 5.39 | 5.586
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | VSEC | 900 | 8900 | 1-1/8" | 7/8" | 63.5 | 6.6 Lb's | 25 Lb's | 425 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.2 | 7 | 15 | 15
|  |  | 460 | 3 | 1.2 | 2.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS007_1FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 6.3 | 6.9 | 7.3 | 8.1
|  |  | R-407A ^ | 6 | 6.5 | 6.9 | 7.2
|  |  | R-448A ^ | 6 | 6.5 | 6.9 | 7.2
|  |  | R-449A ^ | 6 | 6.5 | 6.9 | 7.2
|  |  | R-407C ^ | 5.88 | 6.37 | 6.762 | 7.056
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
1 | 30" | VSEC | 900 | 8800 | 1-1/8" | 7/8" | 63.5 | 8.8 Lb's | 32.6 Lb's | 450 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 1.2 | 7 | 15 | 15
|  |  | 460 | 3 | 1.2 | 2.9 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS010_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 9.6 | 10.5 | 11.1 | 12.2
|  |  | R-407A ^ | 9.1 | 10 | 10.6 | 11
|  |  | R-448A ^ | 9.1 | 10 | 10.6 | 11
|  |  | R-449A ^ | 9.1 | 10 | 10.6 | 11
|  |  | R-407C ^ | 8.918 | 9.8 | 10.388 | 10.78
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | VSEC | 900 | 17900 | 1-3/8" | 1-1/8" | 66.5 | 8.8 Lb's | 33.2 Lb's | 825 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.4 | 14 | 15 | 20
|  |  | 460 | 3 | 2.4 | 5.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS014_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 12.9 | 14.2 | 15 | 16.5
|  |  | R-407A ^ | 12.7 | 14 | 14.8 | 15.4
|  |  | R-448A ^ | 12.7 | 14 | 14.8 | 15.4
|  |  | R-449A ^ | 12.7 | 14 | 14.8 | 15.4
|  |  | R-407C ^ | 12.446 | 13.72 | 14.504 | 15.092
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | VSEC | 900 | 17700 | 1-3/8" | 1-1/8" | 66.5 | 13.3 Lb's | 50.1 Lb's | 850 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.4 | 14 | 15 | 20
|  |  | 460 | 3 | 2.4 | 5.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS015_2FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 14.4 | 15.8 | 16.7 | 18.4
|  |  | R-407A ^ | 14 | 15.6 | 16.3 | 16.9
|  |  | R-448A ^ | 14 | 15.6 | 16.3 | 16.9
|  |  | R-449A ^ | 14 | 15.6 | 16.3 | 16.9
|  |  | R-407C ^ | 13.72 | 15.288 | 15.974 | 16.562
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
2 | 30" | VSEC | 900 | 17500 | 1-3/8" | 1-1/8" | 66.5 | 17.7 Lb's | 65.3 Lb's | 875 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 2.4 | 14 | 15 | 20
|  |  | 460 | 3 | 2.4 | 5.8 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS021_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 19.5 | 21.4 | 22.6 | 24.9
|  |  | R-407A ^ | 19.3 | 21.1 | 22.3 | 23.2
|  |  | R-448A ^ | 19.3 | 21.1 | 22.3 | 23.2
|  |  | R-449A ^ | 19.3 | 21.1 | 22.3 | 23.2
|  |  | R-407C ^ | 18.914 | 20.678 | 21.854 | 22.736
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | VSEC | 900 | 26600 | 1-5/8" | 1-3/8" | 68.3 | 19.9 Lb's | 75.2 Lb's | 1,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.6 | 21 | 21.1 | 25
|  |  | 460 | 3 | 3.6 | 8.7 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS025_3FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 22.1 | 24.3 | 25.6 | 28.2
|  |  | R-407A ^ | 22.5 | 24.7 | 26.1 | 27.2
|  |  | R-448A ^ | 22.5 | 24.7 | 26.1 | 27.2
|  |  | R-449A ^ | 22.5 | 24.7 | 26.1 | 27.2
|  |  | R-407C ^ | 22.05 | 24.206 | 25.578 | 26.656
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
3 | 30" | VSEC | 900 | 26300 | 1-5/8" | 1-3/8" | 68.3 | 26.5 Lb's | 97.9 Lb's | 1,300 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 3.6 | 21 | 22.8 | 25
|  |  | 460 | 3 | 3.6 | 8.7 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS028_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 26 | 28.5 | 30.1 | 33.1
|  |  | R-407A ^ | 25.5 | 28 | 29.5 | 30.7
|  |  | R-448A ^ | 25.5 | 28 | 29.5 | 30.7
|  |  | R-449A ^ | 25.5 | 28 | 29.5 | 30.7
|  |  | R-407C ^ | 24.99 | 27.44 | 28.91 | 30.086
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | VSEC | 900 | 35400 | 1-5/8" | 1-3/8" | 69.5 | 26.6 Lb's | 100.3 Lb's | 1,700 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.8 | 28 | 29.8 | 30
|  |  | 460 | 3 | 4.8 | 11.6 | 15 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS033_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 29.2 | 32 | 33.8 | 37.2
|  |  | R-407A ^ | 29.7 | 32.5 | 34.4 | 35.8
|  |  | R-448A ^ | 29.7 | 32.5 | 34.4 | 35.8
|  |  | R-449A ^ | 29.7 | 32.5 | 34.4 | 35.8
|  |  | R-407C ^ | 29.106 | 31.85 | 33.712 | 35.084
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | VSEC | 900 | 35000 | 1-5/8" | 1-3/8" | 69.5 | 35.3 Lb's | 130.6 Lb's | 1,725 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.8 | 28 | 29.8 | 30
|  |  | 460 | 3 | 4.8 | 11.6 | 15 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS035_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 31.7 | 34.8 | 36.7 | 40.4
R-407A ^ | 31.8 | 34.9 | 36.8 | 38.4
R-448A ^ | 31.8 | 34.9 | 36.8 | 38.4
R-449A ^ | 31.8 | 34.9 | 36.8 | 38.4
R-407C ^ | 31.164 | 34.202 | 36.064 | 37.632 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | VSEC | 900 | 44300 | 2-1/8" | 1-5/8" | 70.5 | 55.5 Lb's | 216.2 Lb's | 2,125 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 6 | 35 | 36.8 | 40
|  |  | 460 | 3 | 6 | 14.5 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS044_5FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 38.2 | 41.9 | 44.3 | 48.7
R-407A ^ | 39.7 | 43.6 | 46 | 47.9
R-448A ^ | 39.7 | 43.6 | 46 | 47.9
R-449A ^ | 39.7 | 43.6 | 46 | 47.9
R-407C ^ | 38.906 | 42.728 | 45.08 | 46.942 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
5 | 30" | VSEC | 900 | 43800 | 2-1/8" | 1-5/8" | 70.5 | 75.9 Lb's | 282 Lb's | 2,150 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 6 | 35 | 36.8 | 40
|  |  | 460 | 3 | 6 | 14.5 | 15.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS052_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 45.9 | 50.3 | 53.1 | 58.4
R-407A ^ | 47.6 | 52.2 | 55.2 | 57.5
R-448A ^ | 47.6 | 52.2 | 55.2 | 57.5
R-449A ^ | 47.6 | 52.2 | 55.2 | 57.5
R-407C ^ | 46.648 | 51.156 | 54.096 | 56.35 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | VSEC | 900 | 52500 | 2-1/8" | 1-5/8" | 71.3 | 91 Lb's | 338.3 Lb's | 2,575 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 42 | 43.8 | 45
|  |  | 460 | 3 | 7.2 | 17.4 | 18.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDS061_7FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDS
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 53.6 | 58.8 | 62 | 68.3
R-407A ^ | 55.5 | 60.9 | 64.3 | 67
R-448A ^ | 55.5 | 60.9 | 64.3 | 67
R-449A ^ | 55.5 | 60.9 | 64.3 | 67
R-407C ^ | 54.39 | 59.682 | 63.014 | 65.66 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | Inlet | Outlet | (dBA) + | (Summer) | (Winter) | Weight
7 | 30" | VSEC | 900 | 61300 | 2-1/8" | 1-5/8" | 71.9 | 106.2 Lb's | 304.7 Lb's | 3,000 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 8.4 | 49 | 50.8 | 60
|  |  | 460 | 3 | 8.4 | 20.3 | 21 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD020_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 18.6 | 20.4 | 21.5 | 23.7
|  |  | R-407A ^ | 17.7 | 19.4 | 20.5 | 21.3
|  |  | R-448A ^ | 17.7 | 19.4 | 20.5 | 21.3
|  |  | R-449A ^ | 17.7 | 19.4 | 20.5 | 21.3
|  |  | R-407C ^ | 17.346 | 19.012 | 20.09 | 20.874
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | VSEC | 900 | 35900 | 1-3/8" | 1-1/8" | 69.5 | 17.7 Lb's | 166.8 Lb's | 1,675 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.8 | 28 | 29.8 | 30
|  |  | 460 | 3 | 4.8 | 11.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD028_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 25.9 | 28.4 | 29.9 | 32.9
|  |  | R-407A ^ | 25.5 | 28 | 29.5 | 30.7
|  |  | R-448A ^ | 25.5 | 28 | 29.5 | 30.7
|  |  | R-449A ^ | 25.5 | 28 | 29.5 | 30.7
|  |  | R-407C ^ | 24.99 | 27.44 | 28.91 | 30.086
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | VSEC | 900 | 35400 | 1-3/8" | 1-1/8" | 69.5 | 26.6 Lb's | 100.3 Lb's | 1,700 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.8 | 28 | 29.8 | 30
|  |  | 460 | 3 | 4.8 | 11.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD032_4FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 28.4 | 31.3 | 32.9 | 36.1
|  |  | R-407A ^ | 28.8 | 31.6 | 33.4 | 34.8
|  |  | R-448A ^ | 28.8 | 31.6 | 33.4 | 34.8
|  |  | R-449A ^ | 28.8 | 31.6 | 33.4 | 34.8
|  |  | R-407C ^ | 28.224 | 30.968 | 32.732 | 34.104
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
4 | 30" | VSEC | 900 | 35000 | 1-3/8" | 1-1/8" | 69.5 | 35.3 Lb's | 355.3 Lb's | 1,725 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 4.8 | 28 | 29.8 | 30
|  |  | 460 | 3 | 4.8 | 11.6 | 15 | 15
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD042_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 38.4 | 42.1 | 44.5 | 48.9
|  |  | R-407A ^ | 37.9 | 41.5 | 43.8 | 45.7
|  |  | R-448A ^ | 37.9 | 41.5 | 43.8 | 45.7
|  |  | R-449A ^ | 37.9 | 41.5 | 43.8 | 45.7
|  |  | R-407C ^ | 37.142 | 40.67 | 42.924 | 44.786
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | VSEC | 900 | 53200 | 1-5/8" | 1-3/8" | 71.3 | 39.9 Lb's | 228 Lb's | 2,550 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 42 | 43.8 | 45
|  |  | 460 | 3 | 7.2 | 17.4 | 18.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD049_6FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  | SIDE VIEW | [5 empty] | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 43.8 | 48 | 50.7 | 55.8
|  |  | R-407A ^ | 44.6 | 48.9 | 51.6 | 53.7
|  |  | R-448A ^ | 44.6 | 48.9 | 51.6 | 53.7
|  |  | R-449A ^ | 44.6 | 48.9 | 51.6 | 53.7
|  |  | R-407C ^ | 43.708 | 47.922 | 50.568 | 52.626
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
6 | 30" | VSEC | 900 | 52500 | 1-5/8" | 1-3/8" | 71.3 | 53 Lb's | 195.8 Lb's | 2,575 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 7.2 | 42 | 43.8 | 45
|  |  | 460 | 3 | 7.2 | 17.4 | 18.1 | 20
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD056_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 51.9 | 56.9 | 60.1 | 66.1
|  |  | R-407A ^ | 51.1 | 56 | 59.1 | 61.6
|  |  | R-448A ^ | 51.1 | 56 | 59.1 | 61.6
|  |  | R-449A ^ | 51.1 | 56 | 59.1 | 61.6
|  |  | R-407C ^ | 50.078 | 54.88 | 57.918 | 60.368
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | VSEC | 900 | 70900 | 1-5/8" | 1-3/8" | 72.5 | 53.2 Lb's | 200.6 Lb's | 3,400 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 9.6 | 56 | 57.8 | 60
|  |  | 460 | 3 | 9.6 | 23.2 | 23.9 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD065_8FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
|  |  | SIDE VIEW |  |  |  |  | END VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
|  |  | Refrig | Fins Per Inch
|  |  | Type | 8 | 10 | 12 | 14
|  |  | R-404A | 58.4 | 64.1 | 67.6 | 74.4
|  |  | R-407A ^ | 59.4 | 65.2 | 68.8 | 71.7
|  |  | R-448A ^ | 59.4 | 65.2 | 68.8 | 71.7
|  |  | R-449A ^ | 59.4 | 65.2 | 68.8 | 71.7
|  |  | R-407C ^ | 58.212 | 63.896 | 67.424 | 70.266
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
8 | 30" | VSEC | 900 | 70000 | 1-5/8" | 1-3/8" | 72.5 | 70.6 Lb's | 261 Lb's | 3,425Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 9.6 | 56 | 57.8 | 60
|  |  | 460 | 3 | 14.4 | 23.2 | 23.9 | 25
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD070_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 63.5 | 69.7 | 73.6 | 80.9
R-407A ^ | 63.6 | 69.8 | 73.7 | 76.8
R-448A ^ | 63.6 | 69.8 | 73.7 | 76.8
R-449A ^ | 63.6 | 69.8 | 73.7 | 76.8
R-407C ^ | 62.328 | 68.404 | 72.226 | 75.264 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | VSEC | 900 | 88600 | 2-1/8" | 1-5/8" | 73.5 | 110.9 Lb's | 432.2 Lb's | 4,250 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 12 | 70 | 71.8 | 75
|  |  | 460 | 3 | 12 | 29 | 29.7 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD087_10FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 76.6 | 84 | 88.7 | 97.5
R-407A ^ | 79.4 | 87 | 91.9 | 95.7
R-448A ^ | 79.4 | 87 | 91.9 | 95.7
R-449A ^ | 79.4 | 87 | 91.9 | 95.7
R-407C ^ | 77.812 | 85.26 | 90.062 | 93.786 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
10 | 30" | VSEC | 900 | 87600 | 2-1/8" | 1-5/8" | 73.5 | 151.7 Lb's | 563.9 Lb's | 4,275 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 12 | 70 | 71.8 | 75
|  |  | 460 | 3 | 12 | 29 | 29.7 | 30
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD105_12FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 91.8 | 100.7 | 106.3 | 117
R-407A ^ | 95.2 | 104.4 | 110.2 | 114.8
R-448A ^ | 95.2 | 104.4 | 110.2 | 114.8
R-449A ^ | 95.2 | 104.4 | 110.2 | 114.8
R-407C ^ | 93.296 | 102.312 | 107.996 | 112.504 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) | (Winter) | Weight
12 | 30" | VSEC | 900 | 105100 | 2-1/8" | 1-5/8" | 74.3 | 182 Lb's | 676.6 Lb's | 5,125 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 14.4 | 84 | 80.1 | 90
|  |  | 460 | 3 | 14.4 | 34.8 | 35.1 | 40
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A

## RDD122_14FAN
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
|  |  | 3885 Crestwood Parkway / Suite 500 |  |  |  |  | Model Series - RDD
|  |  | Duluth, GA 30096 |  |  |  |  | Remote Air Cooled Condenser
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://russell.htpgusa.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
Unit Model Number: | [5 empty] | Tagging Info:
Unit Quantity: | [5 empty] | Date: |  | 2026-07-29 14:18
VERTICAL AIR FLOW CONFIGURATION
SIDE VIEW
PERFORMANCE DATA - THR / MBH @ 1 DEG TD
Refrig | Fins Per Inch
Type | 8 | 10 | 12 | 14
R-404A | 107.1 | 117.4 | 124 | 136.4
R-407A ^ | 111.1 | 121.8 | 128.6 | 134
R-448A ^ | 111.1 | 121.8 | 128.6 | 134
R-449A ^ | 111.1 | 121.8 | 128.6 | 134
R-407C ^ | 108.878 | 119.364 | 126.028 | 131.32 |  |  |  | END VIEW
PHYSICAL DATA
Qty | Fan | Motor | Motor | CFM | Refrig Conn (ODS) * |  | Sound Level | Refrig Chg | Refrig Chg | Net
Fans | Diam | TYPE | RPM |  | (2) Inlets | (2) Outlets | (dBA) + | (Summer) # | (Winter) # | Weight
14 | 30" | VSEC | 900 | 122600 | 2-1/8" | 1-5/8" | 74.9 | 212.3 Lb's | 789.5 Lb's | 5,975 Lb's
ELECTRICAL DATA (60 Hertz)
|  | Design | Volts | Phase | KW | FLA | MCA | MOPD
Voltage
|  |  | 208/230 | 3 | 16.8 | 98 | 100.1 | 110
|  |  | 460 | 3 | 16.8 | 40.6 | 41.3 | 45
Notes | ^ Capacities listed are based upon the Mean Condensing Temperature (average of dew and bubble points at cond inlet)
* Refrigerant connection sizes and quantities are subject to change based upon actual design operating conditions
+ Sound pressure value as measured in horizontal plane 10' away from unit
# Based on R-407A, R-407C, R-448A, R-449A @ +95 / -20 ambient temp / 15 TD. Multiply values by 0.92 for R-404A
Additional Comments:
ACC_SBMTL_1116-A