## Nomenclature (hidden)
Brand |  | Refrigerant Class* |  | Style |  | Fins Per Inch |  | Defrost Type |  | BTUH by Hundreds | Unit Voltage |  | Motor Type |  | Vintage
R | Russell | A | A2L | S | Slim Temp | 6 | 6 FPI | A | Air Defrost | XXX | A | 115/1/60 | D | Dual Speed EC | A
K | Kramer | [6 empty] | E | Electric Defrost (Low Temp) | R-454A | D | 208-230/1/60 | R | Reverse Dual Speed EC
W | Witt

## Engineering (hidden)
Air Defrost Slim Temp | [21 empty] | 115/1 |  |  |  |  | 230/1
Liquid | Legacy Model Number | "DA" Standard Airflow A2L Model Number | "RA" Reverse Airflow A2L Model Number | BTUH Capacity @ +25F ST and 10TD | Actual BTUH | CFM | Suction | Liquid | Distributor Description | Circuits | Standard Nozzles, R454A | Standard Nozzles, R454C | Standard Nozzles, R455A | R454A EEV | R454C/R455A EEV | R454A TXV | R454C/R455A TXV | Valve Size | A2L COMMON Valve Type | A2L COMMON LLS | Fans | Total Fan Amps | Base MCA | Base MOPD | Econet MCA | ECONET MOPD | Total Fan Amps | Base MCA | Base MOPD | Econet MCA | ECONET MOPD | AWEF
100 | ASLA25048 | AS6A053*DA | AS6A053*RA | 5300 | 5355 | 950 | 0.875 | 3/8 | D260-2-3/16 | 2 | 1/2, TYPE L | 3/4, TYPE L | 3/4, TYPE L | SER-A | SER-A | SBFTE-AA-C | SBFVE-AA-C | 0.625 | CSOV-5S | SSOV3S130 | 2 | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20 | 9
| ASLA25061 | AS6A066*DA | AS6A066*RA | 6600 | 6825 | 1000 | 0.875 | 3/8 | D260-2-3/16 | 2 | 3/4, TYPE L | 3/4, TYPE L | 3/4, TYPE L | SER-A | SER-A | SBFTE-AA-C | SBFVE-AA-C | 0.875 | CSOV-7S | SSOV3S130 | 2 | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20 | 9
| ASLA35073 | AS6A080*DA | AS6A080*RA | 8000 | 8085 | 1425 | 0.875 | 3/8 | D260-3-3/16 | 3 | 3/4, TYPE L | 1, TYPE L | 1, TYPE L | SER-A | SER-A | SBFTE-AA-C | SBFVE-A-C | 0.875 | CSOV-7S | SSOV3S130 | 3 | 1.8 | 15 | 20 | 15 | 20 | 0.9 | 15 | 20 | 15 | 20 | 9
| ASLA45098 | AS6A111*DA | AS6A111*RA | 11100 | 11235 | 1900 | 0.875 | 3/8 | D260-4-3/16 | 4 | 1, TYPE L | 1-1/2, TYPE L | 1-1/2, TYPE L | SER-A | SER-A | SBFTE-A-C | SBFVE-A-C | 0.875 | CSOV-7S | SSOV3S130 | 4 | 2.4 | 15 | 20 | 15 | 20 | 1.2 | 15 | 20 | 15 | 20 | 9
| ASLA55122 | AS6A138*DA | AS6A138*RA | 13800 | 13965 | 2375 | 0.875 | 3/8 | D260-6-3/16 | 6 | 1-1/2, TYPE L | 1-1/2, TYPE L | 1-1/2, TYPE L | SER-A | SER-B | SBFTE-A-C | SBFVE-A-C | 0.875 | CSOV-7S | SSOV3S130 | 5 | 3 | 15 | 20 | 15 | 20 | 1.5 | 15 | 20 | 15 | 20 | 9
| ASLA65158 | AS6A176*DA | AS6A176*RA | 17600 | 18165 | 2850 | 0.875 | 3/8 | D260-6-3/16 | 6 | 2, TYPE L | 2, TYPE L | 2-1/2, TYPE L | SER-B | SER-B | SBFTE-A-C | SBFVE-B-C | 1.125 | CSOV-9S | SSOV6S130 | 6 | 3.6 | 15 | 20 | 15 | 20 | 1.8 | 15 | 20 | 15 | 20 | 9
50 | ASLA25048 | AS6A053*DA | AS6A053*RA | 5300 | 5355 | 950 | 0.875 | 3/8 | D260-2-3/16 | 2 | 1/6, TYPE L | 1/6, TYPE L | 1/4, TYPE L | SER-A | SER-A | SBFTE-AA-C | SBFVE-AA-C | 0.625 | CSOV-5S | SSOV3S130 | 2 | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20 | 9
| ASLA25061 | AS6A066*DA | AS6A066*RA | 6600 | 6825 | 1000 | 0.875 | 3/8 | D260-2-3/16 | 2 | 1/4, TYPE L | 1/4, TYPE L | 1/3, TYPE L | SER-A | SER-A | SBFTE-AA-C | SBFVE-AA-C | 0.875 | CSOV-7S | SSOV3S130 | 2 | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20 | 9
| ASLA35073 | AS6A080*DA | AS6A080*RA | 8000 | 8085 | 1425 | 0.875 | 3/8 | D260-3-3/16 | 3 | 1/4, TYPE L | 1/3, TYPE L | 1/3, TYPE L | SER-A | SER-A | SBFTE-AA-C | SBFVE-AA-C | 0.875 | CSOV-7S | SSOV3S130 | 3 | 1.8 | 15 | 20 | 15 | 20 | 0.9 | 15 | 20 | 15 | 20 | 9
| ASLA45098 | AS6A111*DA | AS6A111*RA | 11100 | 11235 | 1900 | 0.875 | 3/8 | D260-4-3/16 | 4 | 1/3, TYPE L | 1/2, TYPE L | 1/2, TYPE L | SER-A | SER-A | SBFTE-A-C | SBFVE-A-C | 0.875 | CSOV-7S | SSOV3S130 | 4 | 2.4 | 15 | 20 | 15 | 20 | 1.2 | 15 | 20 | 15 | 20 | 9
| ASLA55122 | AS6A138*DA | AS6A138*RA | 13800 | 13965 | 2375 | 0.875 | 3/8 | D260-6-3/16 | 6 | 1/2, TYPE L | 1/2, TYPE L | 3/4, TYPE L | SER-A | SER-A | SBFTE-A-C | SBFVE-A-C | 0.875 | CSOV-7S | SSOV3S130 | 5 | 3 | 15 | 20 | 15 | 20 | 1.5 | 15 | 20 | 15 | 20 | 9
| ASLA65158 | AS6A176*DA | AS6A176*RA | 17600 | 18165 | 2850 | 0.875 | 3/8 | D260-6-3/16 | 6 | 3/4, TYPE L | 3/4, TYPE L | 1, TYPE L | SER-B | SER-B | SBFTE-A-C | SBFVE-B-C | 1.125 | CSOV-9S | SSOV3S130 | 6 | 3.6 | 15 | 20 | 15 | 20 | 1.8 | 15 | 20 | 15 | 20 | 9
Electric Defrost Slim Temp | [21 empty] | 230/1
Liquid | Legacy Model Number | "DA" Standard Airflow A2L Model Number | "RA" Reverse Airflow A2L Model Number | BTUH Capacity @ -10F ST and 10TD | Actual BTUH | CFM | Suction | Liquid | Distributor Description | Circuits | Standard Nozzles, R454A | Standard Nozzles, R454C | Standard Nozzles, R455A | R454A EEV | R454C/R455A EEV | R454A TXV | R454C/R455A TXV | Valve Size | A2L COMMON Valve Type | A2L COMMON LLS | Fans | Total Fan Amps | Base MCA | Base MOPD | Econet MCA | ECONET MOPD | Heater Amps | Heater Watts | AWEF
100 | ASLE25046 | AS6E052DDA | AS6E052DRA | 5200 | 5250 | 950 | 0.875 | 3/8 | D260-3-3/16 | 3 | 3/4, TYPE L | 1, TYPE L | 1, TYPE L | SER-A | SER-A | SBFTE-AA-Z | SBFVE-A-Z | 0.875 | CSOV-7S | SSOV3S130 | 2 | 0.6 | 15 | 20 | 15 | 20 | 5.7 | 1300 | 4.02
| ASLE25058 | AS6E065DDA | AS6E065DRA | 6500 | 6615 | 1000 | 0.875 | 3/8 | D260-3-3/16 | 3 | 1, TYPE L | 1-1/2, TYPE L | 1-1/2, TYPE L | SER-A | SER-A | SBFTE-A-Z | SBFVE-A-Z | 1.125 | CSOV-9S | SSOV3S130 | 2 | 0.6 | 15 | 20 | 15 | 20 | 8.6 | 1970 | 4.03
| ASLE35070 | AS6E079DDA | AS6E079DRA | 7900 | 7980 | 1425 | 0.875 | 3/8 | D260-4-3/16 | 4 | 1-1/2, TYPE L | 1-1/2, TYPE L | 2, TYPE L | SER-A | SER-A | SBFTE-A-Z | SBFVE-A-Z | 1.125 | CSOV-9S | SSOV3S130 | 3 | 0.9 | 15 | 20 | 15 | 20 | 8 | 1850 | 4.07
| ASLE45094 | AS6E105DDA | AS6E105DRA | 10500 | 10605 | 1900 | 1.125 | 3/8 | D260-6-3/16 | 6 | 2, TYPE L | 2, TYPE L | 2, TYPE L | SER-A | SER-B | SBFTE-A-Z | SBFVE-B-Z | 1.125 | CSOV-9S | SSOV3S130 | 4 | 1.2 | 15 | 20 | 15.9 | 20 | 10.9 | 2500 | 4.13
| ASLE55117 | AS6E131DDA | AS6E131DRA | 13100 | 13230 | 2375 | 1.125 | 3/8 | D260-6-3/16 | 6 | 2-1/2, TYPE L | 3, TYPE L | 3, TYPE L | SER-A | SER-B | SBFTE-B-Z | SBFVE-B-Z | 1.375 | CSOV-11S | SSOV6S130 | 5 | 1.5 | 15 | 20 | 20 | 25 | 13.9 | 3200 | 4.15
| ASLE65150 | AS6E168DDA | AS6E168DRA | 16800 | 17010 | 2850 | 1.125 | 3/8 | D260-6-3/16 | 6 | 3, TYPE L | 4, TYPE L | 5, TYPE L | SER-B | SER-B | SBFTE-B-Z | SBFVE-B-Z | 1.375 | CSOV-11S | SSOV6S130 | 6 | 1.8 | 15 | 20 | 23 | 25 | 16 | 3700 | 4.15
50 | ASLE25046 | AS6E052DDA | AS6E052DRA | 5200 | 5250 | 950 | 0.875 | 3/8 | D260-3-3/16 | 3 | 1/3, TYPE L | 1/2, TYPE L | 1/2, TYPE L | SER-A | SER-A | SBFTE-AA-Z | SBFVE-AA-Z | 0.875 | CSOV-7S | SSOV3S130 | 2 | 0.6 | 15 | 20 | 15 | 20 | 5.7 | 1300 | 4.02
| ASLE25058 | AS6E065DDA | AS6E065DRA | 6500 | 6615 | 1000 | 0.875 | 3/8 | D260-3-3/16 | 3 | 1/2, TYPE L | 1/2, TYPE L | 3/4, TYPE L | SER-A | SER-A | SBFTE-A-Z | SBFVE-A-Z | 1.125 | CSOV-9S | SSOV3S130 | 2 | 0.6 | 15 | 20 | 15 | 20 | 8.6 | 1970 | 4.03
| ASLE35070 | AS6E079DDA | AS6E079DRA | 7900 | 7980 | 1425 | 0.875 | 3/8 | D260-4-3/16 | 4 | 3/4, TYPE L | 3/4, TYPE L | 3/4, TYPE L | SER-A | SER-A | SBFTE-A-Z | SBFVE-A-Z | 1.125 | CSOV-9S | SSOV3S130 | 3 | 0.9 | 15 | 20 | 15 | 20 | 8 | 1850 | 4.07
| ASLE45094 | AS6E105DDA | AS6E105DRA | 10500 | 10605 | 1900 | 1.125 | 3/8 | D260-6-3/16 | 6 | 3/4, TYPE L | 1, TYPE L | 1, TYPE L | SER-A | SER-A | SBFTE-A-Z | SBFVE-A-Z | 1.125 | CSOV-9S | SSOV3S130 | 4 | 1.2 | 15 | 20 | 15.9 | 20 | 10.9 | 2500 | 4.13
| ASLE55117 | AS6E131DDA | AS6E131DRA | 13100 | 13230 | 2375 | 1.125 | 3/8 | D260-6-3/16 | 6 | 1, TYPE L | 1, TYPE L | 1-1/2, TYPE L | SER-A | SER-A | SBFTE-B-Z | SBFVE-B-Z | 1.375 | CSOV-11S | SSOV3S130 | 5 | 1.5 | 15 | 20 | 20 | 25 | 13.9 | 3200 | 4.15
| ASLE65150 | AS6E168DDA | AS6E168DRA | 16800 | 17010 | 2850 | 1.125 | 3/8 | D260-6-3/16 | 6 | 1-1/2, TYPE L | 1-1/2, TYPE L | 2, TYPE L | SER-B | SER-B | SBFTE-B-Z | SBFVE-B-Z | 1.375 | CSOV-11S | SSOV3S130 | 6 | 1.8 | 15 | 20 | 23 | 25 | 16 | 3700 | 4.15

## Engineering Notes (hidden)
Welbilt RDI Reverse models
| R | A | S | 6 | A=AIR | 0 | * = EITHER | D=DUAL SPEED ECM | A |  |  | Item | Description | Organization | UOM
| K | [10 empty] | ASLA25048ADARA*100 | EVAP,AIR DEF,2F 115/1 2SP REV AIR STOCK | 311 | EA
| W | [5 empty] | A=115 | R= Reverse Dual Speed ECM??? |  |  |  | ASLA25048ADARP*100 | EVAP,AIR DEF,2F 115/1 2SP RP COIL STOCK | 311 | EA
No Brand | C |  |  |  | E-ELEC |  | D=230 |  |  | Russell |  | ASLA25048DDARA*100 | EVAP,AIR DEF,2F 230/1 2SP REV AIR STOCK | 311 | EA
LEGACY | BRAND | A2L | SLIM | FPI | DEFROST | CAPACITY | VOLTAGE | MOTOR | VINTAGE | A2L - Slim Temp |  | ASLA25048DDARP*100 | EVAP,AIR DEF,2F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLA25048*DA | R | A | S | 6 | A | 53 | * | D | A | RAS6A053*DA |  | ASLA25061ADARA*100 | EVAP,AIR DEF,2F 115/1 2SP REV AIR STOCK | 311 | EA
ASLA25061*DA | R | A | S | 6 | A | 66 | * | D | A | RAS6A066*DA |  | ASLA25061ADARP*100 | EVAP,AIR DEF,2F 115/1 2SP RP COILSTOCK | 311 | EA
ASLA35073*DA | R | A | S | 6 | A | 80 | * | D | A | RAS6A080*DA |  | ASLA25061DDARA*100 | EVAP,AIR DEF,2F 230/1 2SP REV AIR STOCK | 311 | EA
ASLA45098*DA | R | A | S | 6 | A | 111 | * | D | A | RAS6A111*DA |  | ASLA25061DDARP*100 | EVAP,AIR DEF,2F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLA55122*DA | R | A | S | 6 | A | 138 | * | D | A | RAS6A138*DA |  | ASLA35073ADARA*100 | EVAP,AIR DEF,3F 115/1 2SP REV AIR STOCK | 311 | EA
ASLA65158*DA | R | A | S | 6 | A | 176 | * | D | A | RAS6A176*DA |  | ASLA35073ADARP*100 | EVAP,AIR DEF,3F 115/1 2SP RP COIL STOCK | 311 | EA
[12 empty] | ASLA35073DDARA*100 | EVAP,AIR DEF,3F 230/1 2SP REV AIR STOCK | 311 | EA
ASLE25046DDA | R | A | S | 6 | E | 52 | D | D | A | RAS6E052DDA |  | ASLA35073DDARP*100 | EVAP,AIR DEF,3F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLE25058DDA | R | A | S | 6 | E | 65 | D | D | A | RAS6E065DDA |  | ASLA45098ADARA*100 | EVAP,AIR DEF,4F 115/1 2SP REV AIR STOCK | 311 | EA
ASLE35070DDA | R | A | S | 6 | E | 79 | D | D | A | RAS6E079DDA |  | ASLA45098ADARP*100 | EVAP,AIR DEF,4F 115/1 2SP RP COIL STOCK | 311 | EA
ASLE45094DDA | R | A | S | 6 | E | 105 | D | D | A | RAS6E105DDA |  | ASLA45098DDARA*100 | EVAP,AIR DEF,4F 230/1 2SP REV AIR STOCK | 311 | EA
ASLE55117DDA | R | A | S | 6 | E | 131 | D | D | A | RAS6E131DDA |  | ASLA45098DDARP*100 | EVAP,AIR DEF,4F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLE66150DDA | R | A | S | 6 | E | 168 | D | D | A | RAS6E168DDA |  | ASLA55122ADARA*100 | EVAP,AIR DEF,5F 115/1 2SP REV AIR STOCK | 311 | EA
[12 empty] | ASLA55122ADARP*100 | EVAP,AIR DEF,5F 115/1 2SP RP COIL STOCK | 311 | EA
[12 empty] | ASLA55122DDARA*100 | EVAP,AIR DEF,5F 230/1 2SP REV AIR STOCK | 311 | EA
ASLA25048*DA | R | A | S | 6 | A | 53 | * | R | A | RAS6A053*RA | REVERSE DUAL SPEED ECM | ASLA55122DDARP*100 | EVAP,AIR DEF,5F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLA25061*DA | R | A | S | 6 | A | 66 | * | R | A | RAS6A066*RA |  | ASLA65158ADARA*100 | EVAP,AIR DEF,6F 115/1 2SP REV AIR STOCK | 311 | EA
ASLA35073*DA | R | A | S | 6 | A | 80 | * | R | A | RAS6A080*RA |  | ASLA65158ADARP*100 | EVAP,AIR DEF,6F 115/1 2SP RP COIL STOCK | 311 | EA
ASLA45098*DA | R | A | S | 6 | A | 111 | * | R | A | RAS6A111*RA |  | ASLA65158DDARA*100 | EVAP,AIR DEF,6F 230/1 2SP REV AIR STOCK | 311 | EA
ASLA55122*DA | R | A | S | 6 | A | 138 | * | R | A | RAS6A138*RA |  | ASLA65158DDARP*100 | EVAP,AIR DEF,6F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLA65158*DA | R | A | S | 6 | A | 178 | * | R | A | RAS6A178*RA |  | ASLE25046DDARA*100 | EVAP,ELE DEF,2F 230/1, 2SP REV AIR STOCK | 311 | EA
[12 empty] | ASLE25046DDARP*100 | EVAP,ELE DEF,2F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLE25046DDA | R | A | S | 6 | E | 52 | D | R | A | RAS6E052DRA |  | ASLE25058DDARA*100 | EVAP,ELE DEF,2F 230/1 2SP REV AIR STOCK | 311 | EA
ASLE25058DDA | R | A | S | 6 | E | 65 | D | R | A | RAS6E065DRA |  | ASLE25058DDARP*100 | EVAP,ELE DEF,2F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLE35070DDA | R | A | S | 6 | E | 79 | D | R | A | RAS6E079DRA |  | ASLE35070DDARA*100 | EVAP,ELE DEF,3F 230/1 2SP REV AIR STOCK | 311 | EA
ASLE45094DDA | R | A | S | 6 | E | 105 | D | R | A | RAS6E105DRA |  | ASLE35070DDARP*100 | EVAP,ELE DEF,3F 208-230/1 2SP RP COIL STOCK | 311 | EA
ASLE55117DDA | R | A | S | 6 | E | 131 | D | R | A | RAS6E131DRA |  | ASLE45094DDARA*100 | EVAP,ELE DEF,4F 230/1 2SP REV AIR STOCK | 311 | EA
ASLE66150DDA | R | A | S | 6 | E | 168 | D | R | A | RAS6E168DRA |  | ASLE45094DDARP*100 | EVAP,ELE DEF,4F 208-230/1 2SP RP COIL STOCK | 311 | EA
[12 empty] | ASLE55117DDARA*100 | EVAP,ELE DEF,5F 230/1 2SP REV AIR STOCK | 311 | EA
[12 empty] | ASLE55117DDARP*100 | EVAP,ELE DEF,5F 208-230/1 2SP RP COIL STOCK | 311 | EA
[12 empty] | ASLE65150DDARA*100 | EVAP,ELE DEF,6F 230/1 2SP REV AIR STOCK | 311 | EA
[12 empty] | ASLE65150DDARP*100 | EVAP,ELE DEF,6F 208-230/1 2SP RP COIL STOCK | 311 | EA

## LAYOUT (hidden)
Slim-Temp
A2L
Catalog Cover |  | COVER
Features |  | Page 1
Nomenclature Page |  | Page 1
AIR | Application | Page 2
AIR | Electrical
AIR | A Voltage
AIR | D Voltage
Electric Defrost | Application | Page 2
Electric Defrost | Electrical
Electric Defrost | D Voltage
AIR | Distributor NZL Selections | Page 3
Electric Defrost | Distributor NZL Selections | Page 4
AIR | Physical Specification | Page 5
Electric Defrost | Physical Specification | Page 5
Dimensionals |  | Page 6
AWEF |  | Page 7

## Application Electrical AIR (hidden)
Application Rating and Electrical Data - Air Defrost Models - 6 FPI
Model Number Dual Speed ECM | BTUH Capacity @ +25F ST and 10TD | CFM | Number of Fans |  | 115V |  |  |  |  | 208-230/1
[5 empty] | Total Fan Motor Amps (1Phase) | MCA | MOPD | Econet Enabled |  | Total Fan Motor Amps (1Phase) | MCA | MOPD | Econet Enabled
| R454A,R454C,R455A | [6 empty] | MCA* | MOPD* |  |  |  | MCA* | MOPD*
[5 empty] | EC Motors |  |  |  |  | EC Motors
RAS6A053ADA | 5300 | 950 | 2 | 1 | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20
RAS6A066ADA | 6600 | 1000 | 2 | 2 | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20
RAS6A080ADA | 8000 | 1425 | 3 | 3 | 1.8 | 15 | 20 | 15 | 20 | 0.9 | 15 | 20 | 15 | 20 |  |  | #REF!
RAS6A111ADA | 11100 | 1900 | 4 | 4 | 2.4 | 15 | 20 | 15 | 20 | 1.2 | 15 | 20 | 15 | 20
RAS6A138ADA | 13800 | 2375 | 5 | 5 | 3 | 15 | 20 | 15 | 20 | 1.5 | 15 | 20 | 15 | 20
RAS6A176ADA | 17600 | 2850 | 6 | 6 | 3.6 | 15 | 20 | 15 | 20 | 1.8 | 15 | 20 | 15 | 20
RAS6E052DDA | 5200 | 950 | 2 | 1 | [5 empty] | 0.6 | 15 | 20 | 15 | 20 | 5.7 | 1300
RAS6E065DDA | 6500 | 1000 | 2 | 2 | [5 empty] | 0.6 | 15 | 20 | 15 | 20 | 8.6 | 1970
RAS6E079DDA | 7900 | 1425 | 3 | 3 | [5 empty] | 0.9 | 15 | 20 | 15 | 20 | 8 | 1850
RAS6E105DDA | 10500 | 1900 | 4 | 4 | [5 empty] | 1.2 | 15 | 20 | 15.9 | 20 | 10.9 | 2500
RAS6E131DDA | 13100 | 2375 | 5 | 5 | [5 empty] | 1.5 | 15 | 20 | 20 | 25 | 13.9 | 3200
RAS6E168DDA | 16800 | 2850 | 6 | 6 | [5 empty] | 1.8 | 15 | 20 | 23 | 25 | 16 | 3700
Model Number Reverse Airflow | BTUH Capacity @ +25F ST and 10TD | CFM | Number of Fans |  | 115V |  |  |  |  | 208-230/1
[5 empty] | Total Fan Motor Amps (1Phase) | MCA | MOPD | Econet Enabled |  | Total Fan Motor Amps (1Phase) | MCA | MOPD | Econet Enabled
| R454A,R454C,R455A | [6 empty] | MCA* | MOPD* |  |  |  | MCA* | MOPD*
[5 empty] | EC Motors |  |  |  |  | EC Motors
RAS6A053*RA | 5300 | 950 | 2 |  | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20
RAS6A066*RA | 6600 | 1000 | 2 |  | 1.2 | 15 | 20 | 15 | 20 | 0.6 | 15 | 20 | 15 | 20
RAS6A080*RA | 8000 | 1425 | 3 |  | 1.8 | 15 | 20 | 15 | 20 | 0.9 | 15 | 20 | 15 | 20
RAS6A111*RA | 11100 | 1900 | 4 |  | 2.4 | 15 | 20 | 15 | 20 | 1.2 | 15 | 20 | 15 | 20
RAS6A138*RA | 13800 | 2375 | 5 |  | 3 | 15 | 20 | 15 | 20 | 1.5 | 15 | 20 | 15 | 20
RAS6A176*RA | 17600 | 2850 | 6 |  | 3.6 | 15 | 20 | 15 | 20 | 1.8 | 15 | 20 | 15 | 20
* Astericks represents variable character based on voltage ordered. See page 2 for nomenclature
Dual Speed EC Motors include thermal overload protection
Note: 208-230 ratings include 2 amp for controls on Econet Enabled units.

## Application Electrical ED (hidden)
Application Rating and Electrical Data - Electric Defrost Models - 6 FPI
Model Number Dual Speed ECM | BTUH Capacity @ -10F ST and 10TD | CFM | Number of Fans | 208-230/1
|  |  |  | Total Fan Motor Amps (1Phase) | Base Model |  | Econet Enabled |  | Heaters
| R454A,R454C,R455A |  |  |  | MCA* | MOPD* | MCA* | MOPD*
|  |  |  | EC Motors |  |  |  |  | Amps | Watts
RAS6E052DDA | 5200 | 950 | 2 | 0.6 | 15 | 20 | 15 | 20 | 5.7 | 1300
RAS6E065DDA | 6500 | 1000 | 2 | 0.6 | 15 | 20 | 15 | 20 | 8.6 | 1970
RAS6E079DDA | 7900 | 1425 | 3 | 0.9 | 15 | 20 | 15 | 20 | 8 | 1850 | 7603.75 | 760.375
RAS6E105DDA | 10500 | 1900 | 4 | 1.2 | 15 | 20 | 15.9 | 20 | 10.9 | 2500
RAS6E131DDA | 13100 | 2375 | 5 | 1.5 | 15 | 20 | 20 | 25 | 13.9 | 3200
RAS6E168DDA | 16800 | 2850 | 6 | 1.8 | 15 | 20 | 23 | 25 | 16 | 3700
Dual Speed EC Motors include thermal overload protection
* MCA/MOPD Represents motor circuit since defrost heaters are powered via condensing unit.
Note: 208-230 ratings include 2 amp for controls on Econet Enabled units.
Model Number Reverse Airflow | BTUH Capacity @ -10F ST and 10TD | CFM | Number of Fans | 208-230/1
|  |  |  | Total Fan Motor Amps (1Phase) | Base Model |  | Econet Enabled |  | Heaters
| R454A,R454C,R455A |  |  |  | MCA* | MOPD* | MCA* | MOPD*
|  |  |  | EC Motors |  |  |  |  | Amps | Watts
RAS6E052DRA | 5200 | 950 | 2 | 0.6 | 15 | 20 | 15 | 20 | 5.7 | 1300
RAS6E065DRA | 6500 | 1000 | 2 | 0.6 | 15 | 20 | 15 | 20 | 8.6 | 1970
RAS6E079DRA | 7900 | 1425 | 3 | 0.9 | 15 | 20 | 15 | 20 | 8 | 1850
RAS6E105DRA | 10500 | 1900 | 4 | 1.2 | 15 | 20 | 15.9 | 20 | 10.9 | 2500
RAS6E131DRA | 13100 | 2375 | 5 | 1.5 | 15 | 20 | 20 | 25 | 13.9 | 3200
RAS6E168DRA | 16800 | 2850 | 6 | 1.8 | 15 | 20 | 23 | 25 | 16 | 3700
Dual Speed EC Motors include thermal overload protection
* MCA/MOPD Represents motor circuit since defrost heaters are powered via condensing unit.
Note: 208-230 ratings include 2 amp for controls on Econet Enabled units.

## Nozzle TXV AIR (hidden)
Distributor Nozzle , Expansion Valves, Electronic Expansion Valves - AIR Defrost 6FPI
Dual Speed ECM and Reverse AirFlow Models
Model Number | Nozzle @ Liquid Temp |  | TXV @ Liquid Temp |  | EEV @ Liquid Temp |  | Number of Circuits
| 50F | 100F | 50F | 100F | 50F | 100F
R454A
RAS6A053**A | 1/6, TYPE L | 1/2 ,TYPE L | SBFTE-AA-C | SBFTE-AA-C | SER-A | SER-A | 2
RAS6A066**A | 1/4, TYPE L | 3/4 ,TYPE L | SBFTE-AA-C | SBFTE-AA-C | SER-A | SER-A | 2
RAS6A080**A | 1/4, TYPE L | 3/4 ,TYPE L | SBFTE-AA-C | SBFTE-AA-C | SER-A | SER-A | 3
RAS6A111**A | 1/3, TYPE L | 1 ,TYPE L | SBFTE-A-C | SBFTE-A-C | SER-A | SER-A | 4
RAS6A138**A | 1/2, TYPE L | 1-1/2 ,TYPE L | SBFTE-A-C | SBFTE-A-C | SER-A | SER-A | 6
RAS6A178**A | 3/4, TYPE L | 2 ,TYPE L | SBFTE-A-C | SBFTE-A-C | SER-B | SER-B | 6
Model Number | Nozzle @ Liquid Temp |  | TXV @ Liquid Temp |  | EEV @ Liquid Temp |  | Number of Circuits
| 50F | 100F | 50F | 100F | 50F | 100F
R454C
RAS6A053**A | 1/6, TYPE L | 3/4 ,TYPE L | SBFVE-AA-C | SBFVE-AA-C | SER-A | SER-A | 2
RAS6A066**A | 1/4, TYPE L | 3/4 ,TYPE L | SBFVE-AA-C | SBFVE-AA-C | SER-A | SER-A | 2
RAS6A080**A | 1/3, TYPE L | 1 ,TYPE L | SBFVE-AA-C | SBFVE-A-C | SER-A | SER-A | 3
RAS6A111**A | 1/2, TYPE L | 1-1/2 ,TYPE L | SBFVE-A-C | SBFVE-A-C | SER-A | SER-A | 4
RAS6A138**A | 1/2, TYPE L | 1-1/2 ,TYPE L | SBFVE-A-C | SBFVE-A-C | SER-A | SER-B | 6
RAS6A178**A | 3/4, TYPE L | 2 ,TYPE L | SBFVE-B-C | SBFVE-B-C | SER-B | SER-B | 6
Model Number | Nozzle @ Liquid Temp |  | TXV @ Liquid Temp |  | EEV @ Liquid Temp |  | Number of Circuits
| 50F | 100F | 50F | 100F | 50F | 100F
R455A
RAS6A053**A | 1/4, TYPE L | 3/4 ,TYPE L | SBFVE-AA-C | SBFVE-AA-C | SER-A | SER-A | 2
RAS6A066**A | 1/3, TYPE L | 1 ,TYPE L | SBFVE-AA-C | SBFVE-AA-C | SER-A | SER-A | 2
RAS6A080**A | 1/3, TYPE L | 1 ,TYPE L | SBFVE-AA-C | SBFVE-AA-C | SER-A | SER-A | 3
RAS6A111**A | 1/2, TYPE L | 1-1/2 ,TYPE L | SBFVE-A-C | SBFVE-A-C | SER-A | SER-A | 4
RAS6A138**A | 3/4, TYPE L | 1-1/2 ,TYPE L | SBFVE-A-C | SBFVE-A-C | SER-A | SER-B | 6
RAS6A178**A | 1, TYPE L | 2-1/2 ,TYPE L | SBFVE-B-C | SBFVE-B-C | SER-B | SER-B | 6
* Astericks represents variable character based on voltage ordered. See page 2 for nomenclature
Air Defrost models based on selection at +25F Suction
Distributor tubes are 3/16" diameter and 14" long

## LOOSE AIR (hidden)
Model Number | Amin Values (Ft2) |  |  |  |  | Loose SSOV (solenoid shut off valve) @ Liquid Temp |  |  | LOOSE CSOV (Check shut off valve)
| 10 Ft Line Run | 20 Ft Line Run | 30 Ft Line Run | 40 Ft Line Run | 50 Ft Line Run | Size | 50F | 100F | Size | Description
R454A
RAS6A053**A | 20.3487 | 26.0422 | 31.7357 | 37.4293 | 43.1228 | 3/8" | SSOV3S130 | SSOV3S130 | 0.625 | CSOV-5S
RAS6A066**A | 22.867 | 28.874 | 34.881 | 40.8881 | 46.8951 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A080**A | 25.8282 | 31.8353 | 37.8423 | 43.8493 | 49.8563 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A111**A | 30.9782 | 36.9852 | 42.9922 | 48.9993 | 55.0063 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A138**A | 36.3535 | 42.3605 | 48.3675 | 54.3745 | 60.3815 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A178**A | 41.8637 | 48.3114 | 54.7592 | 61.2069 | 67.6547 | 3/8" | SSOV3S130 | SSOV6S130 | 1.125 | CSOV-9S
R454C
RAS6A053**A | 19.6612 | 25.1969 | 30.7326 | 36.2683 | 41.804 | 3/8" | SSOV3S130 | SSOV3S130 | 0.625 | CSOV-5S
RAS6A066**A | 22.0718 | 27.8832 | 33.6947 | 39.5061 | 45.3176 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A080**A | 24.9389 | 30.7504 | 36.5618 | 42.3733 | 48.1847 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A111**A | 29.9253 | 35.7367 | 41.5482 | 47.3596 | 53.1711 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A138**A | 35.1297 | 40.9412 | 46.7526 | 52.5641 | 58.3755 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A178**A | 40.4258 | 46.625 | 52.8241 | 59.0232 | 65.2224 | 3/8" | SSOV3S130 | SSOV6S130 | 1.125 | CSOV-9S
R455A
RAS6A053**A | 17.9527 | 22.9945 | 28.0363 | 33.0781 | 38.1198 | 3/8" | SSOV3S130 | SSOV3S130 | 0.625 | CSOV-5S
RAS6A066**A | 20.1598 | 25.4616 | 30.7635 | 36.0654 | 41.3673 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A080**A | 22.7747 | 28.0766 | 33.3784 | 38.6803 | 43.9822 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A111**A | 27.3224 | 32.6242 | 37.9261 | 43.228 | 48.5299 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A138**A | 32.069 | 37.3709 | 42.6728 | 47.9747 | 53.2765 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6A178**A | 36.9113 | 42.5788 | 48.2464 | 53.9139 | 59.5814 | 3/8" | SSOV3S130 | SSOV6S130 | 1.125 | CSOV-9S
Note: Solenoid Shut off valves operate as double duty mitigation / liquid line solenoid valve and are required to ship loose and be installed in the field, outside the refrigerated space.
SSOV/CSOV Selection Criteria: Maximum 10 Ft Line Rise, 100 Foot Line Run, 1:1 Condensing Unit / Evaporator. Contact applications for additional lengths or design considerations.
Amin values calculated using operating conditions included in UL 60335-2-89 101.DVU.1.2 and standard connection sizes (liquid and Suction).
Amin values provided for 10 ft, 20 ft, 30 ft, 40 Ft and 50 Ft line lengths. Contact applications for additional lengths or design considerations.
Amin values intended to determine compliance with UL 2-89 and is NOT for charging calculations.

## Nozzle TXV ED (hidden)
Distributor Nozzle , Expansion Valves, Electronic Expansion Valves - Electric Defrost 6FPI
Dual Speed ECM and Reverse AirFlow Models
Model Number | Nozzle @ Liquid Temp |  | TXV @ Liquid Temp |  | EEV @ Liquid Temp |  | Number of Circuits
| 50F | 100F | 50F | 100F | 50F | 100F
R454A
RAS6E052D*A | 1/3, TYPE L | 3/4, TYPE L | SBFTE-AA-Z | SBFTE-AA-Z | SER-AA | SER-AA | 2
RAS6E065D*A | 1/2, TYPE L | 1, TYPE L | SBFTE-AA-Z | SBFTE-A-Z | SER-AA | SER-A | 2
RAS6E079D*A | 3/4, TYPE L | 1-1/2, TYPE L | SBFTE-AA-Z | SBFTE-A-Z | SER-AA | SER-A | 3
RAS6E105D*A | 3/4, TYPE L | 2, TYPE L | SBFTE-A-Z | SBFTE-A-Z | SER-A | SER-A | 4
RAS6E131D*A | 1, TYPE L | 2-1/2, TYPE L | SBFTE-A-Z | SBFTE-B-Z | SER-A | SER-A | 6
RAS6E168D*A | 1-1/2, TYPE L | 3, TYPE L | SBFTE-B-Z | SBFTE-B-Z | SER-A | SER-B | 6
Model Number | Nozzle @ Liquid Temp |  | TXV @ Liquid Temp |  | EEV @ Liquid Temp |  | Number of Circuits
| 50F | 100F | 50F | 100F | 50F | 100F
R454C
RAS6E052D*A | 1/2, TYPE L | 1, TYPE L | SBFVE-AA-Z | SBFVE-A-Z | SER-AA | SER-AA | 2
RAS6E065D*A | 1/2, TYPE L | 1-1/2, TYPE L | SBFVE-AA-Z | SBFVE-A-Z | SER-AA | SER-A | 2
RAS6E079D*A | 3/4, TYPE L | 1-1/2, TYPE L | SBFVE-A-Z | SBFVE-A-Z | SER-A | SER-A | 3
RAS6E105D*A | 1, TYPE L | 2, TYPE L | SBFVE-A-Z | SBFVE-B-Z | SER-A | SER-A | 4
RAS6E131D*A | 1, TYPE L | 3, TYPE L | SBFVE-B-Z | SBFVE-B-Z | SER-A | SER-B | 6
RAS6E168D*A | 1-1/2, TYPE L | 4, TYPE L | SBFVE-B-Z | SBFVE-C-Z | SER-B | SER-B | 6
Model Number | Nozzle @ Liquid Temp |  | TXV @ Liquid Temp |  | EEV @ Liquid Temp |  | Number of Circuits
| 50F | 100F | 50F | 100F | 50F | 100F
R455A
RAS6E052D*A | 1/2, TYPE L | 1, TYPE L | SBFVE-AA-Z | SBFVE-AA-Z | SER-AA | SER-AA | 2
RAS6E065D*A | 3/4, TYPE L | 1-1/2, TYPE L | SBFVE-AA-Z | SBFVE-A-Z | SER-AA | SER-A | 2
RAS6E079D*A | 3/4, TYPE L | 2, TYPE L | SBFVE-A-Z | SBFVE-A-Z | SER-AA | SER-A | 3
RAS6E105D*A | 1, TYPE L | 2, TYPE L | SBFVE-A-Z | SBFVE-B-Z | SER-A | SER-A | 4
RAS6E131D*A | 1-1/2, TYPE L | 3, TYPE L | SBFVE-A-Z | SBFVE-B-Z | SER-A | SER-B | 6
RAS6E168D*A | 2, TYPE L | 5, TYPE L | SBFVE-B-Z | SBFVE-B-Z | SER-A | SER-B | 6
* Astericks represents variable character based on voltage ordered. See page 2 for nomenclature
Electric Defrost models based on selection at -10F Suction.
Distributor tubes are 3/16" diameter and 14" long

## LOOSE ED (hidden)
Loose Components Required for A2L Mitigation Controls / Amin (Minimum Allowable Room Size) Values
Model Number | Amin Values (Ft2) |  |  |  |  | Loose SSOV (solenoid shut off valve) @ Liquid Temp |  |  | LOOSE CSOV (Check shut off valve)
| 10 Ft Line Run | 20 Ft Line Run | 30 Ft Line Run | 40 Ft Line Run | 50 Ft Line Run | Size | 50F | 100F | Size | Description
R454A
RAS6E052D*A | 19.9298 | 25.6098 | 31.2899 | 36.97 | 42.6501 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6E065D*A | 22.2364 | 28.1294 | 34.0224 | 39.9154 | 45.8084 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E079D*A | 25.0331 | 30.9261 | 36.8191 | 42.7121 | 48.6051 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E105D*A | 29.9235 | 35.8165 | 41.7095 | 47.6025 | 53.4956 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E131D*A | 35.2254 | 41.3923 | 47.5591 | 53.726 | 59.8929 | 3/8" | SSOV3S130 | SSOV3S130 | 1.375 | CSOV-11S
RAS6E168D*A | 40.0394 | 46.2063 | 52.3732 | 58.54 | 64.7069 | 3/8" | SSOV3S130 | SSOV6S130 | 1.375 | CSOV-11S
R454C
RAS6E052D*A | 19.2978 | 24.8201 | 30.3423 | 35.8646 | 41.3869 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6E065D*A | 21.5206 | 27.2291 | 32.9375 | 38.646 | 44.3545 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E079D*A | 24.241 | 29.9495 | 35.658 | 41.3664 | 47.0749 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E105D*A | 28.9981 | 34.7065 | 40.415 | 46.1235 | 51.8319 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E131D*A | 34.1284 | 40.0764 | 46.0243 | 51.9723 | 57.9203 | 3/8" | SSOV3S130 | SSOV3S130 | 1.375 | CSOV-11S
RAS6E168D*A | 38.8111 | 44.7591 | 50.707 | 56.655 | 62.603 | 3/8" | SSOV3S130 | SSOV6S130 | 1.375 | CSOV-11S
R455A
RAS6E052D*A | 17.6068 | 22.636 | 27.6652 | 32.6944 | 37.7235 | 3/8" | SSOV3S130 | SSOV3S130 | 0.875 | CSOV-7S
RAS6E065D*A | 19.6368 | 24.8416 | 30.0464 | 35.2513 | 40.4561 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E079D*A | 22.1138 | 27.3186 | 32.5234 | 37.7282 | 42.9331 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E105D*A | 26.4452 | 31.65 | 36.8548 | 42.0596 | 47.2644 | 3/8" | SSOV3S130 | SSOV3S130 | 1.125 | CSOV-9S
RAS6E131D*A | 31.1243 | 36.555 | 41.9857 | 47.4164 | 52.8471 | 3/8" | SSOV3S130 | SSOV3S130 | 1.375 | CSOV-11S
RAS6E168D*A | 35.3879 | 40.8187 | 46.2494 | 51.6801 | 57.1108 | 3/8" | SSOV3S130 | SSOV6S130 | 1.375 | CSOV-11S
Note: Solenoid Shut off valves operate as double duty mitigation / liquid line solenoid valve and are required to ship loose and be installed in the field, outside the refrigerated space.
SSOV/CSOV Selection Criteria: Maximum 10 Ft Line Rise, 100 Foot Line Run, 1:1 Condensing Unit / Evaporator. Contact applications for additional lengths or design considerations.
Amin values calculated using operating conditions included in UL 60335-2-89 101.DVU.1.2 and standard connection sizes (liquid and Suction).
Amin values provided for 10 ft, 20 ft, 30 ft, 40 Ft and 50 Ft line lengths. Contact applications for additional lengths or design considerations.
Amin values intended to determine compliance with UL 2-89 and is NOT for charging calculations.

## Specifications (hidden)
Specifications
| MODELS - AIR DEFROST 6FPI DUAL SPEED ECM |  |  | TXV Type | Refrigerant Connections |  | Figure Number | Dimensions (Inches) |  |  |  |  | Estimated Shipping Weight (Lbs.)
| Model | Fans | FPI |  | Liquid | Suction |  | Width | Length | Height | Between Mounts (A) | Drain Connection (D)
RAS6A053DA | RAS6A053*DA | 2 | 6 | External | 3/8" | 7/8" | 1 | 54-5/16 | 19-7/8 | 10 | 39 | 27-1/6 | 95
RAS6A066DA | RAS6A066*DA | 2 | 6 | External | 3/8" | 7/8" | 2 | 64-5/16 | 19-7/8 | 10 | 49 | 32-1/6 | 110
RAS6A080DA | RAS6A080*DA | 3 | 6 | External | 3/8" | 7/8" | 3 | 77-5/16 | 19-7/8 | 10 | 31 | 38-2/3 | 135
RAS6A111DA | RAS6A111*DA | 4 | 6 | External | 3/8" | 7/8" | 4 | 100-5/16 | 19-7/8 | 10 | 28-1/4 | 50-1/6 | 160
RAS6A138DA | RAS6A138*DA | 5 | 6 | External | 3/8" | 7/8" | 5 | 123-5/16 | 19-7/8 | 10 | 36 | 61-2/3 | 195
RAS6A178DA | RAS6A178*DA | 6 | 6 | External | 3/8" | 7/8" | 6 | 146-5/16 | 19-7/8 | 10 | 32-3/4 | 73-1/6 | 230 | 73.1562
RAS6A053DA | RAS6A053*RA | 2 | 6 | External | 3/8" | 7/8" | 1 | 54-5/16 | 19-7/8 | 10 | 39 | 27-1/6 | 95
RAS6A066DA | RAS6A066*RA | 2 | 6 | External | 3/8" | 7/8" | 2 | 64-5/16 | 19-7/8 | 10 | 49 | 32-1/6 | 110
RAS6A080DA | RAS6A080*RA | 3 | 6 | External | 3/8" | 7/8" | 3 | 77-5/16 | 19-7/8 | 10 | 31 | 38-2/3 | 135
RAS6A111DA | RAS6A111*RA | 4 | 6 | External | 3/8" | 7/8" | 4 | 100-5/16 | 19-7/8 | 10 | 28-1/4 | 50-1/6 | 160
RAS6A138DA | RAS6A138*RA | 5 | 6 | External | 3/8" | 7/8" | 5 | 123-5/16 | 19-7/8 | 10 | 36 | 61-2/3 | 195
RAS6A178DA | RAS6A178*RA | 6 | 6 | External | 3/8" | 7/8" | 6 | 146-5/16 | 19-7/8 | 10 | 32-3/4 | 73-1/6 | 230
RAS6E052DA | RAS6E052DDA | 2 | 6 | External | 3/8" | 7/8" | 1 | 54-5/16 | 19-7/8 | 10 | 39 | 27-1/6 | 95
RAS6E065DA | RAS6E065DDA | 2 | 6 | External | 3/8" | 7/8" | 2 | 64-5/16 | 19-7/8 | 10 | 49 | 32-1/6 | 110
RAS6E079DA | RAS6E079DDA | 3 | 6 | External | 3/8" | 7/8" | 3 | 77-5/16 | 19-7/8 | 10 | 31 | 38-2/3 | 135
RAS6E105DA | RAS6E105DDA | 4 | 6 | External | 3/8" | 1-1/8" | 4 | 100-5/16 | 19-7/8 | 10 | 28-1/4 | 50-1/6 | 160
RAS6E131DA | RAS6E131DDA | 5 | 6 | External | 3/8" | 1-1/8" | 5 | 123-5/16 | 19-7/8 | 10 | 36 | 61-2/3 | 195
RAS6E168DA | RAS6E168DDA | 6 | 6 | External | 3/8" | 1-1/8" | 6 | 146-5/16 | 19-7/8 | 10 | 32-3/4 | 73-1/6 | 230
RAS6E052DA | RAS6E052DRA | 2 | 6 | External | 3/8" | 7/8" | 1 | 54-5/16 | 19-7/8 | 10 | 39 | 27-1/6 | 95
RAS6E065DA | RAS6E065DRA | 2 | 6 | External | 3/8" | 7/8" | 2 | 64-5/16 | 19-7/8 | 10 | 49 | 32-1/6 | 110
RAS6E079DA | RAS6E079DRA | 3 | 6 | External | 3/8" | 7/8" | 3 | 77-5/16 | 19-7/8 | 10 | 31 | 38-2/3 | 135
RAS6E105DA | RAS6E105DRA | 4 | 6 | External | 3/8" | 1-1/8" | 4 | 100-5/16 | 19-7/8 | 10 | 28-1/4 | 50-1/6 | 160
RAS6E131DA | RAS6E131DRA | 5 | 6 | External | 3/8" | 1-1/8" | 5 | 123-5/16 | 19-7/8 | 10 | 36 | 61-2/3 | 195
RAS6E168DA | RAS6E168DRA | 6 | 6 | External | 3/8" | 1-1/8" | 6 | 146-5/16 | 19-7/8 | 10 | 32-3/4 | 73-1/6 | 230

## AWEF (hidden)
Department of Energy Walk-in Energy |  |  |  | Department of Energy Walk-in Energy
factor (AWEF) Ratings |  |  |  | factor (AWEF) Ratings
COOLER MODELS - AIR and ELECTRIC DEFROST |  |  |  | FREEZER MODELS - ELECTRIC DEFROST
Base Model Number | Defrost Type | FPI | AWEF | Base Model Number | Defrost Type | FPI | AWEF
RAS6A053*DA | Air Defrost | 6 | 9 | RAS6E052DDA | Electric Defrost | 6 | 4.02
RAS6A066*DA | Air Defrost | 6 | 9 | RAS6E065DDA | Electric Defrost | 6 | 4.03
RAS6A080*DA | Air Defrost | 6 | 9 | RAS6E079DDA | Electric Defrost | 6 | 4.07
RAS6A111*DA | Air Defrost | 6 | 9 | RAS6E105DDA | Electric Defrost | 6 | 4.13
RAS6A138*DA | Air Defrost | 6 | 9 | RAS6E131DDA | Electric Defrost | 6 | 4.15
RAS6A178*DA | Air Defrost | 6 | 9 | RAS6E168DDA | Electric Defrost | 6 | 4.15
Department of Energy Walk-in Energy
factor (AWEF) Ratings
COOLER MODELS - ELECTRIC DEFROST
Base Model Number | Defrost Type | FPI | AWEF
RAS6E052DDA | Electric Defrost | 6 | 9
RAS6E065DDA | Electric Defrost | 6 | 9
RAS6E079DDA | Electric Defrost | 6 | 9
RAS6E105DDA | Electric Defrost | 6 | 9
RAS6E131DDA | Electric Defrost | 6 | 9
RAS6E168DDA | Electric Defrost | 6 | 9

## Dimensionals (hidden)
[5 empty] | Standard | #VALUE!
[5 empty] | Reverse | #VALUE!
|  |  | 2 | #VALUE! | 1 | #VALUE!
|  |  | 3 Fan | #VALUE! | 2 | #VALUE!
|  |  | 4 | #VALUE! | 3 | #VALUE!
|  |  | 5 | #VALUE! | 4 | #VALUE!
|  |  | 6 | #VALUE! | 5 | #VALUE!
[5 empty] | 6 | #VALUE!
|  |  | Russell | #VALUE!
|  |  | Witt | #VALUE!
|  |  | Kramer | #VALUE!
|  |  | Coldzone | #VALUE!
New Cabinet is approximately 8" longer on the Electrical End (RH in view above).
NEED AIRFLOW REVERSE AIRFLOW AS WELL (MOVE AIRFLOW ARROW)
Waiting on R&D, assigned to CJ, but not complete as of 09292025
| RAS6A053ADA | RAS6A053ARA
| RAS6A066ADA | RAS6A066ARA
| RAS6A080ADA | RAS6A080ARA
| RAS6A111ADA | RAS6A111ARA
| RAS6A138ADA | RAS6A138ARA
| RAS6A176ADA | RAS6A176ARA
| RAS6E052DDA | RAS6E052DRA
| RAS6E065DDA | RAS6E065DRA
| RAS6E079DDA | RAS6E079DRA
| RAS6E105DDA | RAS6E105DRA
| RAS6E131DDA | RAS6E131DRA
| RAS6E168DDA | RAS6E168DRA
| WAS6A053ADA | WAS6A053ARA
| WAS6A066ADA | WAS6A066ARA
| WAS6A080ADA | WAS6A080ARA
| WAS6A111ADA | WAS6A111ARA
| WAS6A138ADA | WAS6A138ARA
| WAS6A176ADA | WAS6A176ARA
| WAS6E052DDA | WAS6E052DRA
| WAS6E065DDA | WAS6E065DRA
| WAS6E079DDA | WAS6E079DRA
| WAS6E105DDA | WAS6E105DRA
| WAS6E131DDA | WAS6E131DRA
| WAS6E168DDA | WAS6E168DRA
| KAS6A053ADA | KAS6A053ARA
| KAS6A066ADA | KAS6A066ARA
| KAS6A080ADA | KAS6A080ARA
| KAS6A111ADA | KAS6A111ARA
| KAS6A138ADA | KAS6A138ARA
| KAS6A176ADA | KAS6A176ARA
| KAS6E052DDA | KAS6E052DRA
| KAS6E065DDA | KAS6E065DRA
| KAS6E079DDA | KAS6E079DRA
| KAS6E105DDA | KAS6E105DRA
| KAS6E131DDA | KAS6E131DRA
| KAS6E168DDA | KAS6E168DRA
| CAS6A053ADA | CAS6A053ARA
| CAS6A066ADA | CAS6A066ARA
| CAS6A080ADA | CAS6A080ARA
| CAS6A111ADA | CAS6A111ARA
| CAS6A138ADA | CAS6A138ARA
| CAS6A176ADA | CAS6A176ARA
| CAS6E052DDA | CAS6E052DRA
| CAS6E065DDA | CAS6E065DRA
| CAS6E079DDA | CAS6E079DRA
| CAS6E105DDA | CAS6E105DRA
| CAS6E131DDA | CAS6E131DRA
| CAS6E168DDA | CAS6E168DRA
RAS6A053ARA
RAS6A066ARA
RAS6A080ARA
RAS6A111ARA
RAS6A138ARA
RAS6A176ARA
RAS6E052DRA
RAS6E065DRA
RAS6E079DRA
RAS6E105DRA
RAS6E131DRA
RAS6E168DRA
WAS6A053ARA
WAS6A066ARA
WAS6A080ARA
WAS6A111ARA
WAS6A138ARA
WAS6A176ARA
WAS6E052DRA
WAS6E065DRA
WAS6E079DRA
WAS6E105DRA
WAS6E131DRA
WAS6E168DRA
KAS6A053ARA
KAS6A066ARA
KAS6A080ARA
KAS6A111ARA
KAS6A138ARA
KAS6A176ARA
KAS6E052DRA
KAS6E065DRA
KAS6E079DRA
KAS6E105DRA
KAS6E131DRA
KAS6E168DRA
CAS6A053ARA
CAS6A066ARA
CAS6A080ARA
CAS6A111ARA
CAS6A138ARA
CAS6A176ARA
CAS6E052DRA
CAS6E065DRA
CAS6E079DRA
CAS6E105DRA
CAS6E131DRA
CAS6E168DRA
Air Flow

## Submittal
|  |  | HEAT TRANSFER PRODUCTS GROUP, LLC |  |  |  |  | SUBMITTAL DATA SHEET
1550 North Brown Road, Suite 120
Lawrenceville, GA 30043
|  |  | (P) 800-288-9488 / (F) 256-259-7478 | [5 empty] | For Record Only
|  |  | http://htpg.com | [5 empty] | For Approval
Job Name: | [5 empty] | Job Location:
Customer Name: | [5 empty] | Order Number:
Architect / Engineer: | [5 empty] | Prepared By:
RDA
Unit Model Number: | [5 empty] | Tagging Info:
Econet |  | No |  |  |  | Date: |  | 2026-02-27
CAPACITY (BTUH) @ -10 SST/10 TD
| R454A/R454C/R455A |  |  |  |  | Dimensions
| Unit Model |  | 10 TD |  |  | A | W
PHYSICAL DATA
| Unit |  | Refrig Conn (ODS) |  | Drain | Net
| Model |  | Liquid | Suction | Conn | Weight
ELECTRICAL DATA
Number of Fans | Voltage | Phase | Hertz | EC Mtr | Total Motor Amps | MCA | MOPD | Voltage | Heater
|  |  |  | Amps Ea |  |  |  | Code | Amps | Watts
| 208-230 | 1 | 60 |  |  | 15.0 | 20.0 | A
Notes:
Additional Comments: